## Power Monitor
Setting Up the PM 1000
Step 1 - Connect to the Power Monitor
| 1.1 | Set your computers local area connection network adapter within the same subnet as the etehrnet address displayed on the front of the PM 1000, the subnet mask is 255.255.255.0
| 1.2 | Using a standard RJ 45 cable connect to the power monitor using the ethernet port located on the front of the unit.
| 1.3 | Open a web browser and type in the units Ethernet address in the address bar eg http://10.51.xx.xxx
Step 2 - Configure the Analogue Input |  | Note: You must type the http://
Analog Input Configuration
Element | Item Name | Value
0 | Password | 0 | Password default is 0
Range 0 to 9999
1 | Voltage Mode | 2
0 = Direct Delta
1 = Open Delta
2 = Wye
3 = Single Phase
4 = Demo
5 = 1PT1CT-LL
6 = 1PT1CT-LN
2 | PT Primary | 480
Range 1 to 50000
3 | PT Secondary | 480
Range 1 to 600
4 | CT Primary | 250
Range 5 to 50000
5 | System PF Setting | 2
0 = Leading -97 to +89
1 = High -85 to +98
2 = Low -53 to -95
6 | Reserved | 0
Range 0
Set these values and click submit.
Step 3 - Set Correct Ethernet Address
| 3.1 | Using the Ethernet IP List, set the address for the power monitor as seen in the table below eg 10.51.xx.xxx
| 3.2 | set the Gateway IP address to the ethernet card of the rack you wish to communicate with.
| 3.3 | Set the time and date
Ethernet Configuration
Element | Item Name | Value
0 | Password | 0
Range 0 to 9999
1 | IP Address Byte a (aaa.xxx.xxx.xxx) | 10
Range 0 to 255
2 | IP Address Byte b (xxx.bbb.xxx.xxx) | 51
Range 0 to 255
3 | IP Address Byte c (xxx.xxx.ccc.xxx) | xx
Range 0 to 255
4 | IP Address Byte d (xxx.xxx.xxx.ddd) | xxx
Range 0 to 255
5 | Subnet Mask Byte a | 255
Range 0 to 255
6 | Subnet Mask Byte b | 255
Range 0 to 255
7 | Subnet Mask Byte c | 255
Range 0 to 255
8 | Subnet Mask Byte d | 0
Range 0 to 255
9 | Gateway IP Address Byte a | 10
Range 0 to 255
10 | Gateway IP Address Byte b | 51
Range 0 to 255
11 | Gateway IP Address Byte c | xx
Range 0 to 255
12 | Gateway IP Address Byte d | xxx
Range 0 to 255
13 | SNTP Mode Select
0 = Disable
1 = Unicast mode
2 = Anycast mode
14 | SNTP Update Interval | 300
Range 1 to 32766
15 | Time Zone Select
Range 0 to 32
16 | Time Server IP Address Byte a | 0
Range 0 to 255
17 | Time Server IP Address Byte b | 0
Range 0 to 255
18 | Time Server IP Address Byte c | 0
Range 0 to 255
19 | Time Server IP Address Byte d | 0
Range 0 to 255
20 | Demand Broadcast Master Select | 300
0 = Slave
1 = Master
21 | Broadcast Port Number
Range 300 to 400
22 | Reserved | 0
Range 0
Set these values and click submit
Figure 01
Figure 02
This value is specified on the main panel Ct's

## PLC
Environmental Software Installation Guide
Step 1 - Copy User defined data types from master project
ELECTRICITY_TARIFF
ENERGY_MONITORING
ENERGY_MONITORING_DATE_SET
Step 2 - Create Tags
Tag Name | Data Type | Scope | Alias
AIR_FLOW | DINT | Controller
AIR_FLOW_MASK | DINT | Controller
AIR_MONITOR20 | DINT | Controller | In1[xx] (the alias number depends where the air monitor is within the interbus network)
Tdata | DINT[8,10,2] | Controller
EnergyMon | ENERGY_MONITORING | Controller
EnergyMon_Date | ENERGY_MONITORING_DATE_SET | Controller
Power_monitor_Clear | MESSAGE | Controller
Power_Monitor_Read | MESSAGE | Controller
PLA | ELECTRICITY_TARIFF | Controller
TARIFF_BUFFER | DINT[10,2] | Controller
Step 3 - Create New Task
3.1 | Open task properties
Task Name = _100msTask
3.2 | In the configuration tab set:
Type = Periodic
Period = 100ms
Priority = 2
Watchdog = 500ms
Step 4 - Copy power monitor program from master project
Program Name | Scope(Task)
Power_Monitor | _100msTask
Step 5 - Configure Message Blocks
5.1 | Select the Main routine in the Power_Monitor program
5.2 | select the message configuration menu and select the Communication tab
5.3 | Set path to power monitor (Using the IP address allocated in the L405 Ethernet IP List) and apply changes
Note: This must be done for both message instructons.
Step 6 - Copy Routines From Master Project
Routine Name | Scope
U_Environmental | User
U_Tariff_Calc | User
Figure 01 - Rung 0 MSG Configuration
Figure 03 - Common comunication setup for both MSG instructions.
Figure 02 - Rung 1 MSG Configuration

## CMU
CMU Screen
Step 1 - Copy Screens from master project
Screen Name | User Page number
139 - Tariffs | F18
140 - Power Monitoring | F19
141 - Power Monitoring Detail | F20
Step 2 - Configure Local message display
F18 - Tariffs
F19 - Power Monitoring
F20 - Power Monitoring Detail